# Chapter 6: Three-Phase Alternating Current Circuits (Comprehensive Mastery Guide)

Course: Fundamental Electrical Engineering (FunE) • Faculty of Engineering, Khon Kaen University
Instructor: Assoc. Prof. Dr. Nararat Ruangchaijatupon

## 📌 Introduction: Why Three-Phase AC Power? (Intuition from First Principles)

Before memorizing formulas and subscripts, let us understand the physical and economic intuition:

- Single-Phase Power (1ϕ): The standard household supply (230 V) is like “pedaling a bicycle with only one leg”. When the crank reaches the top and bottom dead centers, instantaneous power drops to zero (p(t) pulsates at twice the supply frequency, 2ω). Consequently, large single-phase motors vibrate, run unevenly, and lack inherent starting torque.

- Three-Phase Power (3ϕ): Three identical coils positioned 120∘ apart in space inside an electrical alternator. It acts like a “three-cylinder engine firing sequentially in perfect balance”:

  - Constant Instantaneous Power (p(t)=Constant): In a balanced three-phase system, the total instantaneous power delivered to the load never drops to zero. Large motors operate smoothly without mechanical vibrations and produce self-starting rotating magnetic fields.

  - Massive Conductor Material Savings: Delivering a given amount of power over a transmission line requires 25%−50% less copper or aluminum in a three-phase system compared to a single-phase system carrying the same power at equivalent losses.

  - Two Distinct Voltage Levels from a Single System: A standard 3-phase 4-wire system provides both 230 V (Phase Voltage, line-to-neutral for lights and appliances) and 400 V (Line Voltage, line-to-line for heavy machinery and industrial motors).

Figure 1: Generation of 3-phase voltages from three coils displaced by 120∘ in the generator stator, producing three equal sinusoidal waveforms phase-shifted by 120∘ (From Slide 3).

Figure 2: The three sinusoidal waveforms (va,vb,vc) with period T=360∘, each shifted by 360∘/3=120∘ (From Slide 10).

## 🔤 Complete Subscript & Notation Decoder (Variables Decoded)

The primary reason students struggle with three-phase circuits is confusing subscripts. Let us clarify them permanently:

flowchart LR
    subgraph Source["Source / Generator Side"]
        A_src["Terminal a"]
        B_src["Terminal b"]
        C_src["Terminal c"]
        N_src["Neutral n"]
    end
    subgraph Transmission["Transmission Lines"]
        L_A["Line A (Z_line)"]
        L_B["Line B (Z_line)"]
        L_C["Line C (Z_line)"]
        L_N["Neutral Line (Z_nN)"]
    end
    subgraph Load["Load Side"]
        A_ld["Terminal A"]
        B_ld["Terminal B"]
        C_ld["Terminal C"]
        N_ld["Neutral N"]
    end

    A_src --> L_A --> A_ld
    B_src --> L_B --> B_ld
    C_src --> L_C --> C_ld
    N_src -.-> L_N -.-> N_ld

### 1. Meaning of Subscript Letters

- Lowercase Letters (a,b,c,n): Represent the Source / Generator side, where n is the source neutral point.

- Uppercase Letters (A,B,C,N): Represent the Load / Receiver side, where N is the load neutral point.

- Double Subscripts Represent Potential Difference:

  - Van=Va−Vn : Voltage from source terminal a to source neutral n (Source Phase Voltage).

  - VAN=VA−VN : Voltage across load phase A to load neutral N (Load Phase Voltage).

  - Vab=Va−Vb : Voltage between transmission line a and line b (Line-to-Line Voltage or Line Voltage).

  - VNn=VN−Vn : Voltage difference between load neutral and source neutral (Neutral Shift Voltage).

### 2. Line vs. Phase Quantities Comparison Table

| Quantity | Symbol | Physical Definition | In Star / Wye (Y) Circuit | In Delta (Δ) Circuit |
| --- | --- | --- | --- | --- |
| Phase Voltage | Vp or Vphase | Voltage dropped across one single coil/branch | Measured from phase terminal to neutral (Van) | Measured across individual delta branch (Vab) |
| Line Voltage | VL or Vline | Voltage measured between any two transmission lines | Measured line-to-line, e.g. Vab,Vbc,Vca | Measured line-to-line, e.g. Vab,Vbc,Vca |
| Phase Current | Ip or Iphase | Current flowing through the internal coil winding | Current through single phase arm (Ip=IL) | Current circulating in delta branch (Iab) |
| Line Current | IL or Iline | Current travelling along the external transmission line wire | Current in transmission line (IaA,IbB,IcC) | Current in transmission line (Ia,Ib,Ic) |

## 🧭 Phase Sequence: Positive (abc) vs. Negative (acb)

In a balanced system, all three phase voltages have equal magnitude (Vp) and are displaced by 120∘:

### 1. Positive Sequence (abc Sequence) — Standard in 95% of Problems

The phasor rotates counter-clockwise. Phase a passes the reference axis first, followed by phase b, then phase c:

Van=Vp∠0∘

Vbn=Vp∠−120∘

Vcn=Vp∠−240∘=Vp∠+120∘

### 2. Negative Sequence (acb Sequence) — Used in Exam Trap Questions

Phase a passes first, followed by phase c, then phase b:

Van=Vp∠0∘

Vbn=Vp∠+120∘

Vcn=Vp∠−120∘

Figure 3: Phasor diagrams of positive (abc) vs negative (acb) phase sequences (From Slide 11).

## 🔗 The 4 Interconnection Topologies (Source-to-Load)

Both source and load can be connected in either Star (Y) or Delta (Δ). This yields four possible topologies:

graph TD
    Sources["Source Types:<br/>- Wye (Y)<br/>- Delta (Δ)"] --> Topo["4 Circuit Topologies"]
    Topo --> YY["1. Y - Y Connection (Most Common)"]
    Topo --> YD["2. Y - Δ Connection (High Power)"]
    Topo --> DY["3. Δ - Y Connection"]
    Topo --> DD["4. Δ - Δ Connection"]

Figure 4: A 3-phase 4-wire Y-Y connected system showing source, line impedance, and star-connected load (From Slide 14).

### 1. Mathematical Proof of Wye (Y) System: VL=3Vp∠+30∘

In a Wye-connected source, applying Kirchhoff’s Voltage Law (KVL) between terminal a and terminal b:

Vab=Van−Vbn

For positive sequence with Van=Vp∠0∘ and Vbn=Vp∠−120∘:

Vab=Vp(1+j0)−Vp−12−j32=Vp32+j32

Converting to polar form:

|Vab|=Vp322+322=Vp9+34=Vp3=3Vp

θ=arctan3/23/2=arctan13=30∘

Vab=3Vp∠+30∘

Vbc=3Vp∠−90∘

Vca=3Vp∠+150∘

[!IMPORTANT] Summary for Wye (Y) Connection: * Line Voltage leads Phase Voltage by 30∘: VL=3Vp∠+30∘ * Line Current equals Phase Current: IL=Ip

Figure 5: Graphical phasor proof showing Vab=Van−Vbn=3Vp∠30∘ (From Slide 18).

### 2. Mathematical Proof of Delta (Δ) System: IL=3Ip∠−30∘

In a Delta connection, the phase branches are connected directly between the line conductors:

VL=Vp

Applying Kirchhoff’s Current Law (KCL) at terminal node A:

Ia=IAB−ICA

Assuming balanced positive sequence currents IAB=Ip∠0∘ and ICA=Ip∠+120∘:

Ia=Ip(1+j0)−Ip−12+j32=Ip32−j32=3Ip∠−30∘

[!IMPORTANT] Summary for Delta (Δ) Connection: * Line Voltage equals Phase Voltage: VL=Vp * Line Current lags Phase Current by 30∘: IL=3Ip∠−30∘

Figure 6: Wye source supplying a Delta-connected load (From Slide 15).

Figure 7: Phasor relationship showing Ia=3IAB∠−30∘ (From Slide 22).

Figure 8: Comprehensive summary table of Line vs Phase quantities for Wye and Delta connections (From Slide 23).

### 3. Delta-Wye Impedance Transformation (Δ↔Y)

When solving balanced circuits containing Delta loads, transform the Delta load into an equivalent Wye load to solve on a Per-Phase Equivalent basis:

ZY=ZΔ3⇔ZΔ=3ZY

Figure 9: Transforming a balanced Delta load to an equivalent Wye load ZY=ZΔ/3 (From Slide 34).

## ⚡ Power in Three-Phase Circuits

The total power consumed by a balanced three-phase load (whether connected in Wye or Delta) is three times the single-phase power:

### 1. Complex, Real, and Reactive Power Formulas

S3ϕ=3S1ϕ=3VpIp*=3VLIL∠θ

P3ϕ=3VpIpcosθ=3VLILcosθ [Watts, W]

Q3ϕ=3VpIpsinθ=3VLILsinθ [Volt-Amperes Reactive, VAR]

S3ϕ=P3ϕ2+Q3ϕ2=3VLIL [Volt-Amperes, VA]

[!CAUTION] In the formula 3VLILcosθ, the angle θ is the phase angle of the load impedance (θ=θv−θi of individual phase branch), NOT the angle between line voltage and line current!

Figure 10: Real, reactive, and apparent power formulas for balanced three-phase systems (From Slide 27).

## 📊 Two-Wattmeter Method for Power Measurement

The two-wattmeter method measures the total real and reactive power of a three-phase three-wire system (balanced or unbalanced) using only two wattmeters:

Figure 11: Circuit diagram of the Two-Wattmeter Method with Current Coils (CC) in lines A and C, and Potential Coils (PC) connected across common line B.

Figure 12: Derivation and vector angles of individual wattmeter readings (From Slide 43).

### 1. Wattmeter Reading Equations (Balanced Load, Phase Sequence abc)

- Wattmeter 1 measures line current Ia and voltage Vab:

W1=VabIacos(∠Vab−∠Ia)=VLILcos(30∘−θ)

- Wattmeter 2 measures line current Ic and voltage Vcb:

W2=VcbIccos(∠Vcb−∠Ic)=VLILcos(30∘+θ)

### 2. Master Formulas Derived from W1 and W2

- Total Real Power (Ptotal):

Ptotal=W1+W2

- Total Reactive Power (Qtotal):

Qtotal=3(W1−W2)

- Power Factor Angle (θ):

tanθ=3W1−W2W1+W2⟹pf=cosθ

| Load Power Factor (pf=cosθ) | Load Angle (θ) | Wattmeter 1 Reading (W1) | Wattmeter 2 Reading (W2) | Special Phenomenon |
| --- | --- | --- | --- | --- |
| pf=1.0 (Purely Resistive) | θ=0∘ | W1=W2>0 | W1=W2>0 | Both wattmeters read identical positive values. |
| pf=0.5 (Lagging) | θ=+60∘ | W1>0 | W2=0 | Wattmeter 2 reads exactly ZERO! |
| 0≤pf<0.5 (Lagging) | θ>60∘ | W1>0 | W2<0 (Negative!) | Wattmeter 2 deflects backwards! Reverse CC terminals to read. |
| pf=0 (Purely Reactive) | θ=90∘ | W1=−W2 | W2=−W1 | W1+W2=0 (Zero total real power). |

## ⚙️ Power Factor Correction with Delta Capacitor Banks

Most industrial loads are inductive (induction motors, transformers) operating at lagging power factors. Installing a parallel capacitor bank supplies the required reactive power locally, unloading transmission lines:

Figure 13: Schematic of a three-phase inductive motor load corrected by a parallel Delta-connected capacitor bank.

### 1. Step-by-Step Design Formula

- Calculate the required total reactive power compensation:

QC=P(tanθ1−tanθ2)

- In a Delta-connected capacitor bank, each capacitor sees the full line-to-line voltage (VC=VL):

QC,per phase=QC3=ωCΔVL2⟹CΔ=QC3ωVL2

- If connected in Wye (Y), the voltage across each capacitor is only Vp=VL/3:

CY=QCωVL2=3CΔ

[!TIP] Why Delta is Universally Preferred in Industry: A Delta-connected capacitor bank requires 3× smaller capacitance than a Wye bank (CΔ=13CY) to provide identical reactive VARs. Smaller capacitance means smaller physical size, lighter weight, and lower equipment cost!

## 📝 5 Authentic Exam Problems with Full Step-by-Step Solutions

### 🔴 Problem 1 (Level 1: Fundamentals of Phase Sequence & Line Voltages)

Problem Statement:
A balanced three-phase Wye-connected source has a positive sequence (abc) with phase voltage Van=120∠10∘ V rms.
Find: 1. The remaining phase voltages Vbn and Vcn. 2. All three line-to-line voltages Vab,Vbc,Vca.

#### 💡 Step-by-Step Model Solution:

Step 1: Determine Phase Voltages
In positive sequence, each phase lags by 120∘:

Van=120∠10∘ V

Vbn=120∠(10∘−120∘)=120∠−110∘ V

Vcn=120∠(10∘+120∘)=120∠+130∘ V

Step 2: Calculate Line Voltages
Line voltage magnitude is VL=3Vp=3×120≈207.85 V, leading phase voltage by 30∘:

Vab=3×120∠(10∘+30∘)=207.85∠40∘ V

Vbc=207.85∠(40∘−120∘)=207.85∠−80∘ V

Vca=207.85∠(40∘+120∘)=207.85∠160∘ V

### 🔴 Problem 2 (Level 2: Balanced Y-Y System with Line Impedance - Homework 6 Prob. 1)

Problem Statement:
A balanced 3-phase 4-wire Y-Y system has: * Source: Van=110∠0∘ V rms, abc sequence. * Line impedance: Zline=5−j2 Ω per phase. * Load impedance: ZY=10+j8 Ω per phase. * Neutral wire impedance: Zn=0 Ω.
Find: 1. The line currents IaA,IbB,IcC. 2. The phase voltages at the load terminals VAN,VBN,VCN. 3. The total complex power Stotal delivered to the load.

Figure 14: Balanced Y-Y system with line impedance (Homework 6 Problem 1).

#### 💡 Step-by-Step Model Solution:

Step 1: Single-Phase Equivalent Circuit Analysis
Total impedance per phase:

Ztotal=Zline+ZY=(5−j2)+(10+j8)=15+j6 Ω

Ztotal=152+62∠arctan(6/15)=225+36∠21.8∘=16.16∠21.8∘ Ω

Step 2: Line Current Calculation

IaA=VanZtotal=110∠0∘16.16∠21.8∘=6.81∠−21.8∘ A

IbB=6.81∠(−21.8∘−120∘)=6.81∠−141.8∘ A

IcC=6.81∠(−21.8∘+120∘)=6.81∠98.2∘ A

In=−(IaA+IbB+IcC)=0 A (Balanced!)

Step 3: Load Phase Voltages

VAN=IaAZY=(6.81∠−21.8∘)×(10+j8)

10+j8=100+64∠arctan(8/10)=12.81∠38.66∘ Ω

VAN=6.81×12.81∠(−21.8∘+38.66∘)=87.24∠16.86∘ V

VBN=87.24∠(16.86∘−120∘)=87.24∠−103.14∘ V

VCN=87.24∠(16.86∘+120∘)=87.24∠136.86∘ V

Step 4: Total Complex Power Delivered to the Load

S3ϕ=3×|IaA|2×ZY=3×(6.81)2×(10+j8)=3×46.38×(10+j8)

S3ϕ=1,391.4+j1,113.1 VA=1.39 kW+j1.11 kVAR

### 🔴 Problem 3 (Level 3: Balanced Y-Δ System with Line Impedance)

Problem Statement:
A balanced three-phase system has: * Source: Wye-connected, line-to-line voltage VL=208 V rms, abc sequence, taking Vab as reference (208∠0∘ V). * Line impedance: Zline=1+j1 Ω. * Load: Delta-connected with branch impedance ZΔ=12+j9 Ω.
Find: 1. The line currents Ia,Ib,Ic. 2. The phase currents circulating inside the Delta load IAB,IBC,ICA.

#### 💡 Step-by-Step Model Solution:

Step 1: Transform Delta Load to Equivalent Wye Load

ZY=ZΔ3=12+j93=4+j3 Ω

Step 2: Determine Source Phase Voltage Since Vab=208∠0∘ V and Vab=3Van∠+30∘:

Van=2083∠(0∘−30∘)=120.09∠−30∘ V

Step 3: Total Impedance and Line Current

Ztotal=Zline+ZY=(1+j1)+(4+j3)=5+j4=6.403∠38.66∘ Ω

Ia=VanZtotal=120.09∠−30∘6.403∠38.66∘=18.755∠−68.66∘ A

Ib=18.755∠(−68.66∘−120∘)=18.755∠−188.66∘ A=18.755∠171.34∘ A

Ic=18.755∠(−68.66∘+120∘)=18.755∠51.34∘ A

Step 4: Calculate Delta Phase Currents Phase current magnitude is Ip=IL/3=18.755/3=10.828 A, leading line current by 30∘:

IAB=18.7553∠(−68.66∘+30∘)=10.83∠−38.66∘ A

IBC=10.83∠(−38.66∘−120∘)=10.83∠−158.66∘ A

ICA=10.83∠(−38.66∘+120∘)=10.83∠81.34∘ A

### 🔴 Problem 4 (Level 4: Unbalanced Y-Y System & Neutral Shift - Homework 6 Prob. 2)

Problem Statement:
An unbalanced 3-phase 3-wire Y-Y system (NO neutral wire, Zn=∞) has: * Source: Van=100∠0∘ V, Vbn=100∠−120∘ V, Vcn=100∠120∘ V. * Line impedance: Zline=0 Ω. * Unbalanced load: ZA=10 Ω, ZB=j10 Ω, ZC=−j10 Ω.
Find: 1. The Neutral Shift Voltage (VNn=VN−Vn). 2. The load phase voltages VAN,VBN,VCN. 3. The line currents IaA,IbB,IcC.

Figure 15: Unbalanced Y-Y load with disconnected neutral wire (Homework 6 Problem 2).

#### 💡 Step-by-Step Model Solution:

Step 1: Calculate Load Admittances

YA=110=0.1 S

YB=1j10=−j0.1 S

YC=1−j10=+j0.1 S

Sum of admittances:

∑Y=YA+YB+YC=0.1−j0.1+j0.1=0.1 S

Step 2: Calculate Neutral Shift Voltage using Millman’s Theorem / KCL

VNn=VanYA+VbnYB+VcnYC∑Y

Numerator:

VanYA=(100∠0∘)(0.1)=10

VbnYB=(100∠−120∘)(−j0.1)=(100∠−120∘)(0.1∠−90∘)=10∠−210∘=10∠150∘=−8.66+j5

VcnYC=(100∠120∘)(+j0.1)=(100∠120∘)(0.1∠90∘)=10∠210∘=−8.66−j5

Summing the terms:

Numerator=10+(−8.66+j5)+(−8.66−j5)=10−17.32=−7.32 V

VNn=−7.320.1=−73.2∠0∘=73.2∠180∘ V

Step 3: Calculate Load Phase Voltages

VAN=Van−VNn=100−(−73.2)=173.2∠0∘ V

VBN=Vbn−VNn=(−50−j86.6)−(−73.2)=23.2−j86.6=89.65∠−75∘ V

VCN=Vcn−VNn=(−50+j86.6)−(−73.2)=23.2+j86.6=89.65∠75∘ V

Step 4: Calculate Line Currents

IaA=VANZA=173.2∠0∘10=17.32∠0∘ A

IbB=VBNZB=89.65∠−75∘10∠90∘=8.965∠−165∘ A

IcC=VCNZC=89.65∠75∘10∠−90∘=8.965∠165∘ A

(Verification: IaA+IbB+IcC=17.32+2(−8.66)=0 A. Perfect KCL match!)

### 🔴 Problem 5 (Level 5: Two-Wattmeter Method & Power Factor Correction Exam Problem)

Problem Statement:
A three-phase, 400 V rms,50 Hz supply feeds a balanced inductive load. Two wattmeters connected to measure total input power read:

W1=12.5 kW and W2=4.5 kW

1. Find the total real power Ptotal, reactive power Qtotal, apparent power Stotal, and the power factor. 2. Determine the line current IL. 3. Calculate the required capacitance per phase (CΔ) of a Delta-connected capacitor bank to improve the overall power factor to 0.95 lagging.

#### 💡 Step-by-Step Model Solution:

Step 1: Calculate Total Powers from Wattmeter Readings

Ptotal=W1+W2=12.5+4.5=17.0 kW

Qtotal=3(W1−W2)=3(12.5−4.5)=3×8.0≈13.856 kVAR

Stotal=P2+Q2=17.02+13.8562=289+192=481≈21.93 kVA

pf1=cosθ1=PtotalStotal=17.021.93≈0.775 lagging

θ1=arccos(0.775)≈39.18∘

Step 2: Line Current Before Compensation

IL=Ptotal3VLcosθ1=17,0003×400×0.775=17,000536.94≈31.66 A

Step 3: Capacitor Bank Sizing for pf2=0.95 lagging

θ2=arccos(0.95)≈18.19∘

tanθ1=tan(39.18∘)=0.815

tanθ2=tan(18.19∘)=0.329

Required reactive power compensation:

QC=Ptotal(tanθ1−tanθ2)=17.0×(0.815−0.329)=17.0×0.486=8.262 kVAR

For a Delta-connected capacitor bank (VC=VL=400 V):

CΔ=QC/3ωVL2=8,262/32π×50×4002=2,7542π×50×160,000=2,75450,265,482≈5.48×10−5 F=54.8 μF

## 🎯 Final Exam Key Formulas & Cheat Sheet

- Wye (Y) Relationships:

  - VL=3Vp∠+30∘

  - IL=Ip

- Delta (Δ) Relationships:

  - VL=Vp

  - IL=3Ip∠−30∘

- Δ↔Y Impedance Transformation:

  - ZY=ZΔ3⇔ZΔ=3ZY

- Three-Phase Power:

  - P=3VLILcosθ=3VpIpcosθ

  - Q=3VLILsinθ=3VpIpsinθ

- Two-Wattmeter Method:

  - Ptotal=W1+W2

  - Qtotal=3(W1−W2)

  - tanθ=3W1−W2W1+W2

- Capacitor Sizing:

  - QC=P(tanθ1−tanθ2)

  - CΔ=QC/3ωVL2=CY3